## Assumptions
W_net | 10455 | kW
Generator Effic. | 96 | %
W_out | 10036.8 | kW
TIT | 988.15 | K
P_mc_out | 26500 | kPa
UA_LT | 1550 | kW/K
UA_HT | 1950 | kW/K
Recomp. Effic. | 0.8
Comp. Effic. | 0.71
Turbine Effic. | 0.85
Recomp. Fraction | 0.31
DP_LT_Cold | 0.0113
DP_LT_Hot | 0.0225
DP_HT_Cold | 0.015285
DP_HT_Hot | 0.0326
DP_PC | 0.023
DP_PHX | 0.031

## Results
[6 empty] | T8-T4 | T9-T2
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 45.68 | 3.97 | 6.17 | 1550 | 1950 | 3500 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 47.18 | 9.77 | 10.2 | 1550 | 1950 | 3500 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 47.66 | 15.48 | 17.4 | 1550 | 1950 | 3500 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 48.09 | 20.49 | 25.06 | 1550 | 1950 | 3500 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 48.82 | 23.82 | 32.16 | 1550 | 1950 | 3500 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 49.57 | 25.98 | 39.46 | 1550 | 1950 | 3500 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 49.95 | 28.12 | 48.02 | 1550 | 1950 | 3500 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 50.06 | 29.97 | 57.39 | 1550 | 1950 | 3500 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 49.5 | 31.94 | 65.05 | 1550 | 1950 | 3500 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 48.48 | 35.34 | 76.28 | 1550 | 1950 | 3500 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 44.7 | 38.53 | 93.26 | 1550 | 1950 | 3500 | 0.31
[6 empty] | T8-T4 | T9-T2
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 45.89 | 3.63 | 5.41 | 1750 | 2000 | 3750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 47.44 | 9.15 | 9.18 | 1750 | 2000 | 3750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 47.93 | 14.63 | 16.3 | 1750 | 2000 | 3750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 48.36 | 19.59 | 23.94 | 1750 | 2000 | 3750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 49.07 | 22.92 | 31.02 | 1750 | 2000 | 3750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 49.85 | 24.97 | 38.09 | 1750 | 2000 | 3750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 50.31 | 26.87 | 46.18 | 1750 | 2000 | 3750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 50.33 | 29.05 | 55.89 | 1750 | 2000 | 3750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 49.92 | 31.09 | 63.57 | 1750 | 2000 | 3750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 48.77 | 34.45 | 74.58 | 1750 | 2000 | 3750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 45.01 | 37.7 | 91.38 | 1750 | 2000 | 3750 | 0.31
[6 empty] | T8-T4 | T9-T2
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 46.29 | 1.3 | 4.06 | 2250 | 2500 | 4750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 48.22 | 4.61 | 6.13 | 2250 | 2500 | 4750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 49.09 | 8.58 | 11.77 | 2250 | 2500 | 4750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 49.97 | 11.96 | 17.38 | 2250 | 2500 | 4750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 50.96 | 14.71 | 22.85 | 2250 | 2500 | 4750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 51.79 | 17.15 | 29.07 | 2250 | 2500 | 4750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 52.43 | 18.81 | 35.62 | 2250 | 2500 | 4750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 52.6 | 20.94 | 43.92 | 2250 | 2500 | 4750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 52.36 | 22.72 | 50.27 | 2250 | 2500 | 4750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 51.31 | 26.24 | 60.24 | 2250 | 2500 | 4750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 47.51 | 30.43 | 76.54 | 2250 | 2500 | 4750 | 0.31
[6 empty] | T8-T4 | T9-T2
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 46.53 | 0.43 | 3.22 | 2750 | 3000 | 5750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 48.64 | 2.16 | 4.55 | 2750 | 3000 | 5750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 49.8 | 4.47 | 9.12 | 2750 | 3000 | 5750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 50.92 | 7.04 | 13.73 | 2750 | 3000 | 5750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 52.09 | 9.36 | 18.25 | 2750 | 3000 | 5750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 53.23 | 10.86 | 22.78 | 2750 | 3000 | 5750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 54.01 | 12.42 | 28.24 | 2750 | 3000 | 5750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 54.24 | 14.77 | 35.74 | 2750 | 3000 | 5750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 54.02 | 16.73 | 41.69 | 2750 | 3000 | 5750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 53.2 | 19.79 | 50.13 | 2750 | 3000 | 5750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 49.38 | 24.54 | 66.02 | 2750 | 3000 | 5750 | 0.31
[6 empty] | T8-T4 | T9-T2
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 46.68 | 0.16 | 2.72 | 3250 | 3500 | 6750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 48.86 | 1.06 | 3.77 | 3250 | 3500 | 6750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 50.26 | 2.14 | 7.66 | 3250 | 3500 | 6750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 51.49 | 3.84 | 11.62 | 3250 | 3500 | 6750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 52.85 | 5.51 | 15.32 | 3250 | 3500 | 6750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 54.1 | 6.8 | 19.15 | 3250 | 3500 | 6750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 55.01 | 8.13 | 23.76 | 3250 | 3500 | 6750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 55.39 | 10.23 | 30.23 | 3250 | 3500 | 6750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 55.31 | 11.89 | 35.29 | 3250 | 3500 | 6750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 54.65 | 14.7 | 42.74 | 3250 | 3500 | 6750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 51.03 | 19.15 | 57.17 | 3250 | 3500 | 6750 | 0.31
[6 empty] | T8-T4 | T9-T2
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 46.79 | 0.05 | 2.36 | 3750 | 4000 | 7750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 49.01 | 0.49 | 3.25 | 3750 | 4000 | 7750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 50.36 | 1.13 | 7.1 | 3750 | 4000 | 7750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 51.78 | 2.11 | 10.56 | 3750 | 4000 | 7750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 53.31 | 2.97 | 13.54 | 3750 | 4000 | 7750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 54.67 | 3.97 | 16.83 | 3750 | 4000 | 7750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 55.66 | 5.14 | 20.88 | 3750 | 4000 | 7750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 56.23 | 6.76 | 26.32 | 3750 | 4000 | 7750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 56.24 | 8.3 | 30.86 | 3750 | 4000 | 7750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 55.68 | 10.93 | 37.59 | 3750 | 4000 | 7750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 52.08 | 15.65 | 51.74 | 3750 | 4000 | 7750 | 0.31
[6 empty] | T8-T4 | T9-T2
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 46.88 | 0.02 | 2.07 | 4250 | 4500 | 8750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 49.1 | 0.23 | 2.92 | 4250 | 4500 | 8750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 50.46 | 0.54 | 6.74 | 4250 | 4500 | 8750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 51.96 | 1.03 | 9.92 | 4250 | 4500 | 8750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 53.56 | 1.58 | 12.63 | 4250 | 4500 | 8750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 55.02 | 2.17 | 15.44 | 4250 | 4500 | 8750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 56.1 | 3.06 | 18.99 | 4250 | 4500 | 8750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 56.82 | 4.23 | 23.63 | 4250 | 4500 | 8750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 56.92 | 5.54 | 27.63 | 4250 | 4500 | 8750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 56.51 | 7.85 | 33.6 | 4250 | 4500 | 8750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 53.17 | 11.95 | 46.23 | 4250 | 4500 | 8750 | 0.31
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 46.94 | 0.006 | 1.87 | 4750 | 5000 | 9750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 49.16 | 0.11 | 2.71 | 4750 | 5000 | 9750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 50.51 | 0.27 | 6.57 | 4750 | 5000 | 9750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 52.05 | 0.48 | 9.6 | 4750 | 5000 | 9750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 53.69 | 0.8 | 12.13 | 4750 | 5000 | 9750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 55.21 | 1.16 | 14.69 | 4750 | 5000 | 9750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 56.39 | 1.69 | 17.79 | 4750 | 5000 | 9750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 57.17 | 2.68 | 22.06 | 4750 | 5000 | 9750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 57.42 | 3.47 | 25.32 | 4750 | 5000 | 9750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 57.13 | 5.44 | 30.62 | 4750 | 5000 | 9750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 53.88 | 9.5 | 42.71 | 4750 | 5000 | 9750 | 0.31
CIT (ºC) | Working Fluid |  | CIT (K) | CIP (kPa) | Cycle Efficiency (%) | HT Pinch Point (K) | LT Pinch Point (K) | UA_LT (kW/K) | UA_HT (kW/K) | UA_Total (kW/K) | Recomp. Fraction
35 | 100%CO2 |  | 308.15 | 8500 | 46.98 | 0.002 | 1.73 | 5250 | 5500 | 10750 | 0.31
23.81 | 90%CO2+10%CF4 | 10 | 296.96 | 7882.69 | 49.19 | 0.06 | 2.58 | 5250 | 5500 | 10750 | 0.31
13.81 | 80%CO2+20%CF4 | 20 | 286.96 | 7782.63 | 50.54 | 0.12 | 6.47 | 5250 | 5500 | 10750 | 0.31
3.17 | 70%CO2+30%CF4 | 30 | 276.32 | 7399.22 | 52.08 | 0.25 | 9.47 | 5250 | 5500 | 10750 | 0.31
-7.48 | 60%CO2+40%CF4 | 40 | 265.67 | 6790.9 | 53.76 | 0.39 | 11.88 | 5250 | 5500 | 10750 | 0.31
-17.38 | 50%CO2+50%CF4 | 50 | 255.77 | 6072.33 | 55.31 | 0.61 | 14.29 | 5250 | 5500 | 10750 | 0.31
-26.12 | 40%CO2+60%CF4 | 60 | 247.03 | 5376.98 | 56.54 | 0.92 | 17.15 | 5250 | 5500 | 10750 | 0.31
-34.07 | 29%CO2+71%CF4 | 71 | 239.08 | 4748.51 | 57.43 | 1.51 | 20.91 | 5250 | 5500 | 10750 | 0.31
-38.47 | 21%CO2+79%CF4 | 79 | 234.68 | 4415.41 | 57.7 | 2.28 | 24.04 | 5250 | 5500 | 10750 | 0.31
-42.4 | 10%CO2+90%CF4 | 90 | 230.75 | 4121.62 | 57.59 | 3.64 | 28.47 | 5250 | 5500 | 10750 | 0.31
-43.46 | 100%CF4 |  | 229.69 | 3950 | 54.48 | 7.38 | 39.75 | 5250 | 5500 | 10750 | 0.31